## Slide 1: LF Energy
September, 2020
Digital Substation - Design Team #2
(virtualization)
SEAPATH project
Roadmap

## Slide 2: Context and motivations

## Slide 3: Context
Energy Transition drives change in power transmission and distribution grids. Grid control architecture should adapt swiftly to manage infeed at lower grid voltage levels and greater dynamics in current flow patterns. They should operate more distributed controls in the grids together with a wide range of flexibility services from third-parties.
In this context, TSOs and DSOs require a new generation of Digital Substation Automation Systems (DSAS) that allow more dynamic protection settings and adaptative automation functions. Moreover data management becomes a significant function in itself, both for administration of deployed automation and protection functions, as well as operational grid data.
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)

## Slide 4: Stakes and mainstays of the next DSAS generation
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)
Achieve An “industrial tailor-made” solution
Integrate new
Functions and technologies
Keep pace with the changes of grid uses at reasonable cost
vendor-agnostic implementation and convergence of utility practices
Virtualization
Modular & interoperable architecture (IEC61850)
Open Source
Scalability & Flexibility
Innovation
Time & cost-efficiency
Cross-industry collaboration
Mainstays

## Slide 5: Motivations
5
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)
Stake category | Benefits of open source and virtualization approaches
Time and cost-efficiency | Shared development and maintenance effort through collaboration, avoiding in particular that identical (non-differentiating) functionality is developed and maintained by multiple suppliers duplicating effort.
Time and cost-efficiency | Better reuse of functions enabled by improved modularity and interoperability (e.g. reuse of functions across voltage levels).
Time and cost-efficiency | Remote deployment, supervision, update and upgrade of automation functions and swift switch over between old and new functions, reducing maintenance effort and duration of downgraded service.
Time and cost-efficiency | Automated testing of virtualized functions and systems on digital twin platforms.
Time and cost-efficiency | Pooling of hardware infrastructure and better use of its capabilities.
Cross-industry collaboration | Knowledge sharing and pooling for non-differentiating parts, in compliance with antitrust and procurement regulations.
Cross-industry collaboration | Vendor-and-end-user-agnostic platform implementation, facilitating specification, standardization and integration. Reduced specific requirements and behaviors.
Cross-industry collaboration | Despite less diversity between implementation, mitigation of bugs based of the principle that “with many eyes, all bugs are shallow”.

## Slide 6: Motivations
6
Stake category | Benefits of open source and virtualization approaches
Scalability and flexibility | Simplified central management of a more diverse set of automation system configurations (different applications and settings across substations).
Scalability and flexibility | Split of hardware and software lifecycles facilitating upgradability (replacement of some parts/functions while keeping others, standardization of hardware while diversification of software).
Scalability and flexibility | Enhanced possibility to remotely adapt, disable, enable automation functions according to specific situations (maintenance, failures, etc.).
Scalability and flexibility | Offline simulations e.g. after incidents.
Scalability and flexibility | Simplified LAN design and testing. Modifications of substation automation systems must be tested against the LAN capacity and in the worst case the substation must be tested completely. By aggregating data to virtualization nodes, the impact on LAN transits is reduced and less volatile.
Innovation | Eased deployment of new innovative functions. Better incremental upgradability.
Innovation | Possibility to build digital twins for the simulation of current functions running in the substations in combination with new functions (prototypes, experiments) and of different grid situations.
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)

## Slide 7: High level principles guiding the project

## Slide 8: Project purpose
The aim is to develop a “reference design” and “industrial grade” open source real-time platform that can run virtualized automation and protection applications
    It shall be based on open source components while automation and protection applications could be open or proprietary.
    It shall be preferentially based on existing open source component(s).
    It shall support protection and automation functions.
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)
Notes: Definition of “reference design”: https://en.wikipedia.org/wiki/Reference_design

## Slide 9: Overview of the new grid control architecture based on virtualization
Substation Level
Key Requirements
Data Center Level
integration
deployment
test
Substation Level
…
Supervision & control center
IT integration & orchestration center
Key Requirements
Data Center Level
Ctrl
Supervision
Monitoring
SCADA
Digital Twin
Prot
Prot
Ctrl
monitoring
SCADA
Centralized automation
Automaton
Automaton
Implementations based on the “reference” platform from LFE project
Prot
Auto
Ctrl
monitoring
SCADA
Prot
Prot
Auto
Ctrl
monitoring
SCADA
Prot
Prot
Auto
Ctrl
monitoring
SCADA
Prot
Prot
Auto
Ctrl
monitoring
SCADA
Prot
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)

## Slide 10: Project activities
The project will encompass the following activities:
    Specifying the requirements to be fulfilled by the reference platform (see next slide)
    Specifying the test procedures needed to assess the fulfillment of the requirements
    Building the appropriate system(s) architecture(s) for the software platform and specifying requirements for hardware architecture
    Developing code for the specific functions and services to be delivered by the platform
    Defining and implementing APIs to external applications
    Performing the integration of the software platform
    Testing the fulfillment of the requirements after the implementation, as a proof-of-concept, of a realistic protection and automation system on top of the integrated software platform [additionally each party may share with the project their internal test results based on proprietary implementations]
    Defining guidelines and best practices to test, integrate, deploy, and maintain the applications on such platform
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)

## Slide 11: Functional requirements (for a first minimum viable product)

## Slide 12: Examples of substation systems to be considered for a minimum viable product
Example #1 (from RTE) - Typical 63kV substation
    The typical substation includes feeders for up to 5 lines. The layout is one breaker per feeder. Disconnectors between feeders may be included. Each feeder implements the following functions :
      Distance protection A
      Distance protection B (different algorithm) or Line Differential B
      Recloser
      Breaker failure protection
      Overloading protection
    For each feeder, 2 (redundant) sampled value streams (electrical parameter measurements) up to 10 Mbit/s are collected
    The following functions are implemented at the substation level :
      Gateway to external central or local systems (IEC 61850, 104, etc.)
      Local control (HMI, recordings …)
      IEC 61131 automation
      Phasor Measurement Unit
      Misc. (fault location algorithm, slow area automation)
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)
Notes: In Europe, 63 kV substations (or equivalent High Voltage) may be operated by the transmission or distribution operators, depending on national regulations. Thousands of substations of this kind are in use in Europe (approx. 1200 in France). The need for virtualization at this level is driven by the development of renewable energy at distribution level.
Although simplified, the performance requirements of protective functions at HV substations remain similar to those of EHV substations.
Being less critical than EHV substations in case of failures, innovation is easier at HV substations.

## Slide 13: Examples of substation systems to be considered for a minimum viable product
Example #2 (from National Grid) – Typical 400kV substation
    Typical substation may have 4+ feeders and 4 transformers
    Feeder bay functions:
      Unit Protection
      Distance protection or second unit protection
      Delayed Auto Reclose (DAR)
      Breaker failure protection
      Backup protection (O/C, E/F, Dist)
      Feeder end / stub protection
      Phase unbalance alarm
      BCU, CBU, synch and volt selection
    Other functions :​
      Gateway to external central or local systems (IEC 61850, 104, 101)​
      HMI, data recording and logging, health and diagnostic alarms
      Phasor Measurement Unit​
      Misc. (fault location, QoS, DSM)​
      ATCC (Automatic Tap Change Control)
      ARS (Automatic Reactive Switching where applicable)
      Busbar Protection
      Interlocking
    TX bay
      CB fail
      Pole discrepancy / Phases not together
      Phase unbalance alarm
      connections prot (unit)
      TX O/A prot
      REF (restricted earth fault)
      backup O/C
      Interface for mechanical prot (gas, oil surge, winding temp etc.)
      Trip cct supervision
      Ferro resonance
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)

## Slide 14: Examples of substation systems to be considered for a minimum viable product
Example #3 (from Liander) - This is a typical substation for Liander (exceptions are possible).
Substation characteristics
Substation size:
Station voltage level up to 40 bays; usually around 15 to 25 bays of 10/20 kV
Some stations contain 50 kv bays
Voltage levels: 10kV, 20kV and 50 kV
2 to 3 transformers
Per typical bay
Current measurement (Current measurement frequency: 1500 Hz)
2x overcurrent protection
Voltage measurement
Current measurement
Functions below varies per substation
Protection:
Transformer protection: Buchholz
Distance Protection
Line differential protection
Busbar protection
Frequency protection
Earth fault protection
Transformer differential protection
Direction controlled overcurrent protection
General Functions:
Voltage regulator
Interlocking
Synchrocheck
PQ measurement (not MVP)
Voltage measurement
Frequency measurement
Partial discharge measurement (not MVP)
Pressure measurements (Air/SF6)
Transformer oil temperature measurement
PMU
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)

## Slide 15: Requirement list
The project will specify the requirements to be fulfilled by the reference platform including:
    Application isolation
    Performance & accuracy
    Availability / Redundancy
    Scalability
    Time synchronization
    Data exchange
    Supervision
    Application deployment and orchestration
    Configuration services
    Cybersecurity services
    Long Term Support and Lifecycle management
    Coexistence with conventional devices (failover or hybrid deployment)
15
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)

## Slide 16: Functional Requirements References for the first MVP
Virtualized platform shall meet the following functional requirements for the first MVP.
Performance requirements
  Message transfer time performance shall meet IEC 61850-5 clause-11.2 to the corresponding application class
    Protection-11.2.1 & 11.2.4; Automation – 11.2.2; Operator-11.2.3; commands-11.2.6
  Time synch performance shall meet IEC 61850-5 clause-11.1.3.3 to the corresponding application class
  Data integrity with allowed residual error probability shall meet IEC 61850-5 clause-11.3.2 to the corresponding application class
  Reliability to the corresponding application class
    Security for protection scheme (e.g. unwanted trips of protection) shall meet clause-11.3.3.2
    Dependability for protection scheme (e.g. missing trips of protection) shall meet clause-11.3.3.3
  Availability shall meet IEC 61850-5 clause-11.3.4
  Communication system: failures, station/bay level, process level, recovery delay, redundancy shall meet IEC 61850-5 clause-11.4
Data model (semantics, addressing, self-description, admin) shall meet IEC 61850-5 clause-12
NOTE: Above requirements are as per IEC 61850 Ed2.0; clauses number will be updated upon latest release of the standard
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)
Notes: Minutes on DT2 meeting on 2020-02- 28: one amendment: it is agreed that the project will not assess the requirements on EMC, construction, environmental base on the assumption that the software will be compatible with hardware fulfilling these requirements (and considering also that the hardware infrastructure for visualization may be subject to less stringent requirements).

## Slide 17: System architecture and technology stack (for a first minimum viable product)

## Slide 18: Virtualization architecture
  Hardware virtualization + OS-level virtualization
  Software (SW)
  Hardware (HW)
RT OS
App m
App Services
Type-1 Hypervisor + Linux (real-time) + container daemon
CPU
DRAM
NIC
Storage
CPU
DRAM
CPU
DRAM
Prot. Device 1
Prot. Device 1
Prot. Device n
RT OS
Container technology
App 1
Container technology
Prot. Device n
OS
App 1
OS
App m
Network management
Network drivers + devices
RT applications ; jitter < 1ms
RT network ; jitter < 100µs
Applications with no RT requirements
OS
RT OS
Virtual machines that can host applications (RT or not RT)
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)
Notes: An application can be hosted in a :
virtual machine (guest). This guest runs on top of the hypervisor. They are 2 options to reduce the overhead:
  Passthrough :the guest interact directly with the hardware. Cons : the guest is not hardware independent anymore
  Paravirtualization : hypervisor exposes a modified version of the physical hardware interface to the guest. Cons : the guest needs to be compatible
container. A container can be run directly on the host or in a guest:
  Pros: small overhead , small size
  Cons: use the kernel of the host (not possible to run windows container directly on a Linux host and vice versa) , less isolation
The network can be handled by :
the host drivers. However the 100µs jitter for sample value (61850 9-2) is difficult to achieve with this configuration.
DPDK and a virtual switch (OVS-DPDK) : CPUs and memory and NIC are dedicated to OVS-DPDK. In this configuration 100µs jitter for sample value is a realistic target.

## Slide 19: Technical architecture and stack
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)
Platform services
Firmware
Hardware
Best effort CPUs
Real time CPUs
Real time purpose memory
General purpose memory
Process NIC
Administration NIC
Low latency 61850 stack (100µs)
VM administration
synchronization (ptp)
Redundancy (cluster)
Container administration
Network administration
Non-platform / Third party services
Gateway
Automation App
Protection App
OT monitoring
App
…
…
Fault detection & recovery
Platform monitoring
Cybersecurity
Data center services
Deployment
Monitoring
Cybersecurity
Orchestration

## Slide 20: Technology options
Hardware/chip architecture options:
  x86 is retained as the reference chip architecture for the MVP
  The project should nevertheless consider that the platform should support ARM architecture in a second stage
Hypervisor options:
  Linux / PREEMPT_RT is retained as the reference kernel for the MVP
  Other options are discarded for the time being: Xenomai seems to have little industrial support, ACRN is not mature enough to date though promising (thus it should be kept in the radar for a later stage)
Linux distribution:
  Yocto provides a reference set of tools to build Linux distributions for embedded critical systems
  Two options are identified for the core distribution of the project: building a specific distribution using Yocto tools or reusing the core distribution from CIP (https://www.cip-project.org/) which relies on Yocto  The decision is to start with Yocto for prototyping the MVP and to engage a discussion with CIP in parallel in order to assess the possibility of reusing CIP.
Platform and application orchestration:
  Kubernetes is considered as the reference choice for container orchestration
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)
Notes: Pros for reusing CIP: leveraging the long term maintenance effort from CIP (10 years support)
Cons for reusing CIP: old Kernel version and possibly missing support on needed firmware of software component
Need to engage with CIP once requirements are cleared in order to assess pros and cons

## Slide 21: Configuration and test
Configuration tools needed to:
    set up the platform
    build the firmware
    integrate real time and best effort applications (VM or container)
Testing tools to :
    assess the performance of the platform
    achieve function tests
Automatic tests based on common scenarii
Development of new scenarii and automation of commissioning and maintenance routines
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)

## Slide 22: Priorities and contributions (to reach the minimum viable product)

## Slide 23: Priorities at the launch of the project for the development of a Minimum Viable Product
Project activity / topic | Priority rank | Comment
Specifying the requirements to be fulfilled by the reference platform | 1st priority | 0.7 FTEs of expert and architect contribution
Specifying the test procedures needed to assess the fulfillment of the requirements | 1st priority | 
Building the appropriate system(s) architecture(s) for the software platform and specifying requirements for hardware architecture | 1st priority | 
Developing code for the specific functions and services to be delivered by the platform | 2nd priority | 
Defining and implementing APIs to external applications | 2nd priority | 
Performing the integration of the software platform | 1st priority | Contribution of a preliminary integrated platform (packaged Linux distribution and associated building scripts, including also generic performance testing tools) 2 FTEs contributing to the integration and testing of the platform.
Testing the fulfillment of the requirements for automation applications after the implementation, as a proof-of-concept, of a realistic automation system on top of the integrated software platform | 1st priority (*) | 
Testing the fulfillment of the requirements for protection applications after the implementation, as a proof-of-concept, of a realistic protection and automation system on top of the integrated software platform | 2nd priority | 
Defining guidelines and best practices to test, integrate, deploy, and maintain the applications on such platform | 2nd priority | 
© 2019-2020 Advantech, Alliander, GE, National Grid, RTE, Schneider Electric, Siemens, licensed under Creative Commons Attribution 4.0 International (CC BY 4.0)
Notes: (*) Although the MVP targets both automation and protection applications, with a realistic ambition to reach a qualified industrial-grade implementation by end of 2023, the project should strive to qualify an intermediate version of the platform for automation applications by end of 2021.